## 200MINCALCULATOR
UAF Airflow Calculator
Data Input
|  |  |  | Frame Face Interference | [6 empty] | Air Filter
Filter Dimensions |  |  |  | (Uni-grid Negligible) | [6 empty] | Length | Width
Length |  | Width |  | 0.5 |  | Perimeter/Face Flange Width |  |  |  |  | 12 | 12
13 |  | 13 |  | 0.25 |  | Horizontal Intermediate Width |  |  |  |  | Intermediates Square Inch Area
[6 empty] | 0 |  | Qty |  |  | 0 | 0
300 |  | Cubic Feet/Minute |  | 0.25 |  | Verticle Intermediate Width
[6 empty] | 0 |  | Qty |  |  | 144 | Square Inches
[11 empty] | 1 | Square Feet
Calculations
Face Velocity
Open Surface Area |  |  | 300 |  | Cubic Feet (ft^3)
144 |  | Square Inches |  |  | min |  |  |  | 300 | ft/min
1 |  | Square Feet | 1 |  | Sq.Ft (ft^2)
UAF Pressure Drop Estimation
|  |  |  | Inches of H20 |  |  | Pascals
| 1/8" 45 PPI Quadrafoam |  |  | No Data
| 1/8" 60 PPI Quadrafoam |  |  | No Data
| 1/8" 80 PPI Quadrafoam |  |  | No Data
| 1/4" 10 PPI Quadrafoam |  |  | 0.017139 |  |  | 4.274
| 1/4" 25 PPI Quadrafoam |  |  | 0.029909 |  |  | 7.4582
| 1/4" 45 PPI Quadrafoam |  |  | 0.070132 |  |  | 17.4885
| 1/4" 60 PPI Quadrafoam |  |  | 0.13485 |  |  | 33.6261
| 1/4" 80 PPI Quadrafoam |  |  | 0.21009 |  |  | 52.3896
| 3/8" 10 PPI Quadrafoam |  |  | 0.029887 |  |  | 7.4527
| 3/8" 25 PPI Quadrafoam |  |  | 0.059731 |  |  | 14.895
| 3/8" 45 PPI Quadrafoam |  |  | 0.085334 |  |  | 21.2793
| 3/8" 60 PPI Quadrafoam |  |  | 0.19507 |  |  | 48.6441
| 3/8" 80 PPI Quadrafoam |  |  | No Data
| 1/2" 10 PPI Quadrafoam |  |  | 0.037947 |  |  | 9.4627
| 1/2" 25 PPI Quadrafoam |  |  | 0.085209 |  |  | 21.2482
| 1/2" 45 PPI Quadrafoam |  |  | 0.15522 |  |  | 38.7066
| 1/2" 60 PPI Quadrafoam |  |  | 0.25 |  |  | 62.3409
| 1/2" 80 PPI Quadrafoam |  |  | No Data
| UFM-25 White Polyester |  |  | 0.079564 |  |  | 19.8406
| UFM-50 White Polyester |  |  | 0.12529 |  |  | 31.2429
| UFM-100 White Polyester |  |  | 0.13965 |  |  | 34.8244
CALCULATOR - DO NOT TOUCH
| 1/8" 45 PPI Quadrafoam |  |  | No Data
| 1/8" 60 PPI Quadrafoam |  |  | No Data
| 1/8" 80 PPI Quadrafoam |  |  | No Data
| 1/4" 10 PPI Quadrafoam |  |  | 0.017139
| 1/4" 25 PPI Quadrafoam |  |  | 0.029909
| 1/4" 45 PPI Quadrafoam |  |  | 0.070132
| 1/4" 60 PPI Quadrafoam |  |  | 0.13485
| 1/4" 80 PPI Quadrafoam |  |  | 0.21009
| 3/8" 10 PPI Quadrafoam |  |  | 0.029887
| 3/8" 25 PPI Quadrafoam |  |  | 0.059731
| 3/8" 45 PPI Quadrafoam |  |  | 0.085334
| 3/8" 60 PPI Quadrafoam |  |  | 0.19507
| 3/8" 80 PPI Quadrafoam |  |  | No Data
| 1/2" 10 PPI Quadrafoam |  |  | 0.037947
| 1/2" 25 PPI Quadrafoam |  |  | 0.085209
| 1/2" 45 PPI Quadrafoam |  |  | 0.15522
| 1/2" 60 PPI Quadrafoam |  |  | 0.25
| 1/2" 80 PPI Quadrafoam |  |  | No Data
| UFM-25 White Polyester |  |  | 0.079564
| UFM-50 White Polyester |  |  | 0.12529
| UFM-100 White Polyester |  |  | 0.13965
Online Polynomial Regression Tool
http://www.xuru.org/rt/PR.asp